## Summary
| SAM Grid Outage Annual Unmet Load |  | PV capacity (kW):
|  |  | 5 | 10 | 15 | 20 | 25 | 30
| Battery Capacity (kWh): | 20 | 33.13% | 10.32% | 5.85% | 4.309% | 3.487% | 2.922%
|  | 40 | 31.31% | 4.647% | 0.5737% | 0.2158% | 0.09872% | 0.03596%
|  | 60 | 30.91% | 3.394% | 0.05186% | 1.743e-05% | 0% | 1.276e-05%
|  | 80 | 30.65% | 2.811% | 4.504e-05% | 1.743e-05% | 0% | 1.276e-05%
|  | 100 | 30.42% | 2.452% | 4.504e-05% | 1.743e-05% | 0% | 1.276e-05%
per battery capacity (kWh)
10
annual load (kWh)
10840
| HOMER Annual Unmet Load |  | PV capacity (kW): 5: PV capacity (kW):
(battery count) |  |  | 5 | 10 | 15 | 20 | 25 | 30
2 | Battery Capacity (kWh): | 20 | 33.79% | 10.05% | 5.138% | 3.561% | 2.74% | 2.205%
4 |  | 40 | 32.35% | 5.046% | 0.6734% | 0.2214% | 0.1107% | 0.04613%
6 |  | 60 | 31.92% | 3.865% | 0.09225% | 0% | 0% | 0%
8 |  | 80 | 31.59% | 3.275% | 0% | 0% | 0% | 0%
10 |  | 100 | 31.25% | 2.841% | 0% | 0% | 0% | 0%
| SAM Grid Target Annual Unmet Load |  | PV capacity (kW): 5: PV capacity (kW):
|  |  | 5 | 10 | 15 | 20 | 25 | 30
| Battery Capacity (kWh): | 20 | 32.56% | 11.1% | 6.798% | 5.162% | 4.265% | 3.641%
|  | 40 | 30.41% | 4.5% | 0.6592% | 0.2854% | 0.1417% | 0.07942%
|  | 60 | 29.95% | 3.116% | 0.1181% | 0.02196% | 0% | 0%
|  | 80 | 29.7% | 2.499% | 1.811e-05% | 1.515e-05% | 0% | 0%
|  | 100 | 29.48% | 2.111% | 1.811e-05% | 1.515e-05% | 0% | 0%

## HOMER_results_SAM_HOMER_compari
# | PV kW | Custom 10 kWh | Converter kW | Total Capital Cost $ | Total NPC $ | Tot. Ann. Cap. Cost $/yr | Tot. Ann. Repl. Cost $/yr | Total O&M Cost $/yr | Total Fuel Cost $/yr | Total Ann. Cost $/yr | Operating Cost $/yr | COE $/kWh | PV Production kWh/yr | Tot. Electrical Production kWh/yr | AC Primary Load Served kWh/yr | Ren. Fraction | Cap. Shortage kWh/yr | Cap. Shortage Frac. | Unmet Load kWh/yr | Unmet Load Frac. | Excess Electricity kWh/yr | CO2 Emissions kg/yr | CO Emissions kg/yr | UHC Emissions kg/yr | PM Emissions kg/yr | SO2 Emissions kg/yr | NOx Emissions kg/yr | Battery Autonomy hr | Battery Throughput kWh/yr | Battery Life yr
1 | 5 | 2 | 100 | 10600 | 12458 | 829 | 145 | 0 | 0 | 975 | 145 | 0.136 | 8246 | 8246 | 7178 | 1 | 4308 | 0 | 3663 | 0.34 | 272 | 0 | 0 | 0 | 0 | 0 | 0 | 14.55 | 3445 | 9.6
2 | 5 | 4 | 100 | 11200 | 12812 | 876 | 126 | 0 | 0 | 1002 | 126 | 0.137 | 8246 | 8246 | 7334 | 1 | 4124 | 0 | 3507 | 0.32 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 29.09 | 3620 | 18.2
3 | 5 | 6 | 100 | 11800 | 13417 | 923 | 127 | 0 | 0 | 1050 | 127 | 0.142 | 8246 | 8246 | 7380 | 1 | 4069 | 0 | 3460 | 0.32 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 43.64 | 3673 | 20
4 | 5 | 8 | 100 | 12400 | 14099 | 970 | 133 | 0 | 0 | 1103 | 133 | 0.149 | 8246 | 8246 | 7416 | 1 | 4026 | 0 | 3424 | 0.32 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 58.18 | 3713 | 20
5 | 5 | 10 | 100 | 13000 | 14782 | 1017 | 139 | 0 | 0 | 1156 | 139 | 0.155 | 8246 | 8246 | 7452 | 1 | 3985 | 0 | 3388 | 0.31 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 72.73 | 3754 | 20
6 | 10 | 2 | 100 | 20600 | 24309 | 1611 | 290 | 0 | 0 | 1902 | 290 | 0.195 | 16491 | 16491 | 9751 | 1 | 1256 | 0 | 1089 | 0.1 | 5518 | 0 | 0 | 0 | 0 | 0 | 0 | 14.55 | 5506 | 6
7 | 10 | 4 | 100 | 21200 | 24735 | 1658 | 276 | 0 | 0 | 1935 | 276 | 0.188 | 16491 | 16491 | 10293 | 1 | 631 | 0 | 547 | 0.05 | 4881 | 0 | 0 | 0 | 0 | 0 | 0 | 29.09 | 6114 | 10.8
8 | 10 | 6 | 100 | 21800 | 25085 | 1705 | 257 | 0 | 0 | 1962 | 257 | 0.188 | 16491 | 16491 | 10421 | 1 | 485 | 0 | 419 | 0.04 | 4749 | 0 | 0 | 0 | 0 | 0 | 0 | 43.64 | 6258 | 15.8
9 | 10 | 8 | 100 | 22400 | 25470 | 1752 | 240 | 0 | 0 | 1992 | 240 | 0.19 | 16491 | 16491 | 10486 | 1 | 411 | 0 | 355 | 0.03 | 4693 | 0 | 0 | 0 | 0 | 0 | 0 | 58.18 | 6331 | 20
10 | 10 | 10 | 100 | 23000 | 26152 | 1799 | 247 | 0 | 0 | 2046 | 247 | 0.194 | 16491 | 16491 | 10533 | 1 | 357 | 0 | 308 | 0.03 | 4657 | 0 | 0 | 0 | 0 | 0 | 0 | 72.73 | 6383 | 20
11 | 15 | 2 | 100 | 30600 | 35742 | 2394 | 402 | 0 | 0 | 2796 | 402 | 0.272 | 24737 | 24737 | 10283 | 1 | 641 | 0 | 557 | 0.05 | 13170 | 0 | 0 | 0 | 0 | 0 | 0 | 14.55 | 5761 | 5.7
12 | 15 | 4 | 100 | 31200 | 36151 | 2441 | 387 | 0 | 0 | 2828 | 387 | 0.263 | 24737 | 24737 | 10767 | 1 | 84 | 0 | 73 | 0.01 | 12584 | 0 | 0 | 0 | 0 | 0 | 0 | 29.09 | 6305 | 10.4
13 | 15 | 6 | 100 | 31800 | 36480 | 2488 | 366 | 0 | 0 | 2854 | 366 | 0.263 | 24737 | 24737 | 10830 | 1 | 11 | 0 | 10 | 0 | 12508 | 0 | 0 | 0 | 0 | 0 | 0 | 43.64 | 6376 | 15.5
14 | 15 | 8 | 100 | 32400 | 36841 | 2535 | 347 | 0 | 0 | 2882 | 347 | 0.266 | 24737 | 24737 | 10840 | 1 | 0 | 0 | 0 | 0 | 12496 | 0 | 0 | 0 | 0 | 0 | 0 | 58.18 | 6387 | 20
15 | 15 | 10 | 100 | 33000 | 37523 | 2581 | 354 | 0 | 0 | 2935 | 354 | 0.271 | 24737 | 24737 | 10840 | 1 | 0 | 0 | 0 | 0 | 12496 | 0 | 0 | 0 | 0 | 0 | 0 | 72.73 | 6387 | 20
16 | 20 | 2 | 100 | 40600 | 47115 | 3176 | 510 | 0 | 0 | 3686 | 510 | 0.353 | 32983 | 32983 | 10455 | 1 | 447 | 0 | 386 | 0.04 | 21236 | 0 | 0 | 0 | 0 | 0 | 0 | 14.55 | 5768 | 5.7
17 | 20 | 4 | 100 | 41200 | 47490 | 3223 | 492 | 0 | 0 | 3715 | 492 | 0.343 | 32983 | 32983 | 10816 | 1 | 28 | 0 | 24 | 0 | 20799 | 0 | 0 | 0 | 0 | 0 | 0 | 29.09 | 6174 | 10.7
18 | 20 | 6 | 100 | 41800 | 47814 | 3270 | 470 | 0 | 0 | 3740 | 470 | 0.345 | 32983 | 32983 | 10840 | 1 | 0 | 0 | 0 | 0 | 20769 | 0 | 0 | 0 | 0 | 0 | 0 | 43.64 | 6201 | 15.9
19 | 20 | 8 | 100 | 42400 | 48211 | 3317 | 455 | 0 | 0 | 3771 | 455 | 0.348 | 32983 | 32983 | 10840 | 1 | 0 | 0 | 0 | 0 | 20769 | 0 | 0 | 0 | 0 | 0 | 0 | 58.18 | 6201 | 20
20 | 20 | 10 | 100 | 43000 | 48893 | 3364 | 461 | 0 | 0 | 3825 | 461 | 0.353 | 32983 | 32983 | 10840 | 1 | 0 | 0 | 0 | 0 | 20769 | 0 | 0 | 0 | 0 | 0 | 0 | 72.73 | 6201 | 20
21 | 25 | 2 | 100 | 50600 | 58480 | 3958 | 616 | 0 | 0 | 4575 | 616 | 0.434 | 41228 | 41228 | 10543 | 1 | 345 | 0 | 297 | 0.03 | 29392 | 0 | 0 | 0 | 0 | 0 | 0 | 14.55 | 5745 | 5.7
22 | 25 | 4 | 100 | 51200 | 58834 | 4005 | 597 | 0 | 0 | 4602 | 597 | 0.425 | 41228 | 41228 | 10829 | 1 | 14 | 0 | 12 | 0 | 29047 | 0 | 0 | 0 | 0 | 0 | 0 | 29.09 | 6066 | 10.9
23 | 25 | 6 | 100 | 51800 | 59158 | 4052 | 576 | 0 | 0 | 4628 | 576 | 0.427 | 41228 | 41228 | 10840 | 1 | 0 | 0 | 0 | 0 | 29033 | 0 | 0 | 0 | 0 | 0 | 0 | 43.64 | 6079 | 16.2
24 | 25 | 8 | 100 | 52400 | 59582 | 4099 | 562 | 0 | 0 | 4661 | 562 | 0.43 | 41228 | 41228 | 10840 | 1 | 0 | 0 | 0 | 0 | 29033 | 0 | 0 | 0 | 0 | 0 | 0 | 58.18 | 6079 | 20
25 | 25 | 10 | 100 | 53000 | 60264 | 4146 | 568 | 0 | 0 | 4714 | 568 | 0.435 | 41228 | 41228 | 10840 | 1 | 0 | 0 | 0 | 0 | 29033 | 0 | 0 | 0 | 0 | 0 | 0 | 72.73 | 6079 | 20
26 | 30 | 2 | 100 | 60600 | 69845 | 4741 | 723 | 0 | 0 | 5464 | 723 | 0.515 | 49474 | 49474 | 10601 | 1 | 278 | 0 | 239 | 0.02 | 37581 | 0 | 0 | 0 | 0 | 0 | 0 | 14.55 | 5722 | 5.8
27 | 30 | 4 | 100 | 61200 | 70185 | 4787 | 703 | 0 | 0 | 5490 | 703 | 0.507 | 49474 | 49474 | 10835 | 1 | 6 | 0 | 5 | 0 | 37298 | 0 | 0 | 0 | 0 | 0 | 0 | 29.09 | 5985 | 11
28 | 30 | 6 | 100 | 61800 | 70510 | 4834 | 681 | 0 | 0 | 5516 | 681 | 0.509 | 49474 | 49474 | 10840 | 1 | 0 | 0 | 0 | 0 | 37292 | 0 | 0 | 0 | 0 | 0 | 0 | 43.64 | 5991 | 16.5
29 | 30 | 8 | 100 | 62400 | 70952 | 4881 | 669 | 0 | 0 | 5550 | 669 | 0.512 | 49474 | 49474 | 10840 | 1 | 0 | 0 | 0 | 0 | 37292 | 0 | 0 | 0 | 0 | 0 | 0 | 58.18 | 5991 | 20
30 | 30 | 10 | 100 | 63000 | 71635 | 4928 | 675 | 0 | 0 | 5604 | 675 | 0.517 | 49474 | 49474 | 10840 | 1 | 0 | 0 | 0 | 0 | 37292 | 0 | 0 | 0 | 0 | 0 | 0 | 72.73 | 5991 | 20

## SAM_HOMER_comparison_SAM_PV+ES
run | Desired bank capacity (kWh) | Desired array size (kWdc) | Critical load unmet percentage (year 1) (%) | LCOE Levelized cost of energy real (cents/kWh) | Net capital cost ($)
1 | 20 | 5 | 33.1269 | 354.067 | 35025.2
2 | 40 | 5 | 31.308 | 421.867 | 41666.1
3 | 60 | 5 | 30.9131 | 476.41 | 46963.8
4 | 80 | 5 | 30.6538 | 540.014 | 53163.1
5 | 100 | 5 | 30.4211 | 595.373 | 58549.2
6 | 20 | 10 | 10.3207 | 245.242 | 48632.6
7 | 40 | 10 | 4.6472 | 279.628 | 55273.6
8 | 60 | 10 | 3.394 | 306.764 | 60571.3
9 | 80 | 10 | 2.8106 | 338.482 | 66770.6
10 | 100 | 10 | 2.4517 | 366.109 | 72156.7
11 | 20 | 15 | 5.8496 | 207.32 | 62240.1
12 | 40 | 15 | 0.57374 | 230.063 | 68881
13 | 60 | 15 | 0.051861 | 248.09 | 74178.8
14 | 80 | 15 | 4.5035e-05 | 269.202 | 80378.1
15 | 100 | 15 | 4.5035e-05 | 287.648 | 85764.2
16 | 20 | 20 | 4.3088 | 188.361 | 75847.6
17 | 40 | 20 | 0.21578 | 205.199 | 82488.5
18 | 60 | 20 | 1.7427e-05 | 218.584 | 87786.3
19 | 80 | 20 | 1.7427e-05 | 234.291 | 93985.6
20 | 100 | 20 | 1.7427e-05 | 248.018 | 99371.6
21 | 20 | 25 | 3.4865 | 177.059 | 89455.1
22 | 40 | 25 | 0.098724 | 190.395 | 96096
23 | 60 | 25 | 0 | 201.048 | 101394
24 | 80 | 25 | 0 | 213.562 | 107593
25 | 100 | 25 | 0 | 224.496 | 112979
26 | 20 | 30 | 2.922 | 169.52 | 103063
27 | 40 | 30 | 0.035961 | 180.591 | 109704
28 | 60 | 30 | 1.2755e-05 | 189.438 | 115001
29 | 80 | 30 | 1.2755e-05 | 199.837 | 121201
30 | 100 | 30 | 1.2755e-05 | 208.923 | 126587

## SAM_HOMER_comparison_SAM_PV+ES_
run | Desired bank capacity (kWh) | Desired array size (kWdc) | Electricity load total in each year (kWh) | Electricity load total in each year (kWh)_1 | Annual energy imported from grid (kWh) | Annual energy imported from grid (kWh)_2 | LCOE Levelized cost of energy real (cents/kWh) | Net capital cost ($) | Unmet Load (calc)
1 | 20 | 5 | 0 | 10829.3 | 0 | 3526.37 | 347.818 | 35025.2 | 0.32563
2 | 40 | 5 | 0 | 10829.3 | 0 | 3293.5 | 414.724 | 41666.1 | 0.30413
3 | 60 | 5 | 0 | 10829.3 | 0 | 3243.83 | 468.388 | 46963.8 | 0.29954
4 | 80 | 5 | 0 | 10829.3 | 0 | 3216.74 | 530.951 | 53163.1 | 0.29704
5 | 100 | 5 | 0 | 10829.3 | 0 | 3192.52 | 585.372 | 58549.2 | 0.2948
6 | 20 | 10 | 0 | 10829.3 | 0 | 1202.1 | 240.42 | 48632.6 | 0.111
7 | 40 | 10 | 0 | 10829.3 | 0 | 487.322 | 274.442 | 55273.6 | 0.045
8 | 60 | 10 | 0 | 10829.3 | 0 | 337.461 | 301.181 | 60571.3 | 0.031162
9 | 80 | 10 | 0 | 10829.3 | 0 | 270.662 | 332.358 | 66770.6 | 0.024993
10 | 100 | 10 | 0 | 10829.3 | 0 | 228.626 | 359.521 | 72156.7 | 0.021112
11 | 20 | 15 | 0 | 10829.3 | 0 | 736.198 | 203.289 | 62240.1 | 0.067982
12 | 40 | 15 | 0 | 10829.3 | 0 | 71.3871 | 225.759 | 68881 | 0.006592
13 | 60 | 15 | 0 | 10829.3 | 0 | 12.7871 | 243.494 | 74178.8 | 0.0011808
14 | 80 | 15 | 0 | 10829.3 | 0 | 0.0019611 | 264.246 | 80378.1 | 1.8109e-07
15 | 100 | 15 | 0 | 10829.3 | 0 | 0.0019611 | 282.365 | 85764.2 | 1.8109e-07
16 | 20 | 20 | 0 | 10829.3 | 0 | 559.016 | 184.796 | 75847.6 | 0.051621
17 | 40 | 20 | 0 | 10829.3 | 0 | 30.9053 | 201.411 | 82488.5 | 0.0028539
18 | 60 | 20 | 0 | 10829.3 | 0 | 2.3777 | 214.592 | 87786.3 | 0.00021956
19 | 80 | 20 | 0 | 10829.3 | 0 | 0.001641 | 230.035 | 93985.6 | 1.5153e-07
20 | 100 | 20 | 0 | 10829.3 | 0 | 0.001641 | 243.525 | 99371.6 | 1.5153e-07
21 | 20 | 25 | 0 | 10829.3 | 0 | 461.828 | 173.75 | 89455.1 | 0.042646
22 | 40 | 25 | 0 | 10829.3 | 0 | 15.3455 | 186.933 | 96096 | 0.001417
23 | 60 | 25 | 0 | 10829.3 | 0 | 0 | 197.423 | 101394 | 0
24 | 80 | 25 | 0 | 10829.3 | 0 | 0 | 209.724 | 107593 | 0
25 | 100 | 25 | 0 | 10829.3 | 0 | 0 | 220.471 | 112979 | 0
26 | 20 | 30 | 0 | 10829.3 | 0 | 394.288 | 166.401 | 103063 | 0.036409
27 | 40 | 30 | 0 | 10829.3 | 0 | 8.6011 | 177.334 | 109704 | 0.00079424
28 | 60 | 30 | 0 | 10829.3 | 0 | 0 | 186.047 | 115001 | 0
29 | 80 | 30 | 0 | 10829.3 | 0 | 0 | 196.272 | 121201 | 0
30 | 100 | 30 | 0 | 10829.3 | 0 | 0 | 205.203 | 126587 | 0